# RESIDENTIAL SERVICES

| Type of Service & Socket | Approved Voltage | Optional Voltage w/Utility Approval |
| --- | --- | --- |
|  | 120/240V 1 PH 3W 4 Terminal | 120/208V 1 PH 3W 5 Terminal |
| 100 Amp Socket Only, Overhead | Surface | SUAT121-OGWR (Note 3: MS14TB) | EC659-0121 |
|  | Flush | NA | NA |
| 100 Amp Meter Socket & Circuit Breaker Combination, Overhead | Surface | JA1224B1100SEC, JC0406L125SEC, JA1224B1125SEC, JA1632B1100SEC, JA1632B1125SEC | 5THJAW = ECMC5J |
|  | Flush | JA1224B1100FEC, JA1632B1100FEC, JC0406L125FEC JA1224B1125FEC, JA1632B1125FEC | 5THJAW = ECMC5J |
| 100 Amp Socket Only, Underground | Surface | NA | NA |
|  | Flush | NA | NA |
| 100 Amp Meter Socket & Circuit Breaker Combination, Underground | Surface | JA1224B1100SEC, JC0406L125SEC JA1224B1125SEC, JA1632B1100SEC, JA1632B1125SEC, | 5THJAW = ECMC5J |
|  | Flush | JA1224B1100FEC, JA1632B1100FEC, JC0406L125FEC JA1224B1125FEC, JA1632B1125FEC, | 5THJAW = ECMC5J |
| 200 Amp Socket Only, Overhead | Surface | SUAT327-OGWR (Note 3: MS24TB) | EC659-0121 |
|  | Flush | NA | NA |
| 200 Amp Meter Socket & Circuit Breaker Combination, Overhead | Surface | JC0406L1200SEC JC2442B1200SEC, JA3040B1200SECW, JA4040B1200SECW | 5THJAW = ECMC5J |
|  | Flush | JC0406L1200FEC JC2442B1200FEC | 5THJAW = ECMC5J |
| 200 Amp Socket Only, Underground | Surface | NA | NA |
|  | Flush | NA | NA |
| 200 Amp Meter Socket & Circuit Breaker Combination, Underground | Surface | JC0406L1200SEC, JA1212L1200SED, JA2040B1200SED, JA3042B1200SED, JA3042B1225SED | 5THJAW = ECMC5J |
|  | Flush | JC0406L1200FEC, JA1212L1200FED, JA2040B1200FED, JA3042B1200FED, JA3042B1225FED | 5THJAW = ECMC5J |
| 400 Amp Socket Only, Overhead | Surface | NA | NA |
|  | Flush | NA | NA |
| 400 Amp Socket Only, Underground | Surface | NA | NA |
|  | Flush | NA | NA |
| 400 Amp Meter Socket & Circuit Breaker Combination, Underground Only | Surface | BY1451GL BY1455GL | NA |
|  | Flush | JC0404L1400FDS JA0816B1400FDS JA3042B1400SDS JA3042B1400FDS | NA |
| 400 Amp Meter Socket & Circuit Breaker Combination Underground or Overhead | Surface | JC0404L1400SCS JA0816B1400SCS JA3042B1400SCS | NA |

NA:  Not Available

Note:  This list of approved manufacturer’s meter equipment is indicative of many of the types of equipment that is acceptable but is not an exhaustive list of all possible acceptable versions manufactured by a particular company.  The general guidelines to consider when selecting meter equipment not shown is that PacifiCorp:

- Requires EUSERC approved metering equipment

- Requires manual link bypasses on 400 ampere--lever bypasses and automatic bypasses not allowed.

- Manual link bypass sockets are recommended on all residential services; no interruption of power for meter maintenance

- Requires that all non-residential meter sockets shall have manual link bypass or safety socket.

- Requires ANSI detachable type meter socket--no A-base or K-base sockets.

- Requires all sockets shall be ring types--ringless not allowed.

- Allows single and poly-phase direct connect sockets up to a maximum of 225 amperes.

- Allows 400 ampere direct connect sockets with manual link bypasses for single phase only.

- Requires that safety sockets be on all commercial poly-phase services and on single-phase 480-volt services.

COMMERCIAL SERVICES

| Type of Service | Approved Voltages | Optional Voltages with Utility Approval |
| --- | --- | --- |
|  | 120/240V 1PH 3W 4 Terminal | 120/208V 3PH 4W Wye 7 Terminal | 277/480V 3PH 4W Wye 7 Terminal | 120/408V 1 PH 3W 5 Terminal | 240/480V 1PH 3W 4 Terminal | 120/240V 3PH 4W Delta 7 Terminal | 240/480V 3PH 4W Delta 7 Terminal |
| 100 Amp Socket Only, Overhead | Surface | BY110GK OR MS14TB | BY110JK OR MS17TB | NA | BY110GK W/UX001WL OR MS14TB W/UX001WL | BY110GK OR MS14TB | BY110JK OR MS17TB | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 100 Amp Meter Socket & Circuit Breaker Combination, Overhead | Surface | BY111GK OR MM0202L11-00EY | BY111JK OR MM0303L31-00EY | NA | BY111GU w/X001WL | NA | BY11JU | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 100 Amp Socket Only, Underground | Surface | BY110GK OR MS14TB | BY110JK OR MS17TB | NA | BY110GK w/UX001WL OR MS14TB W/UX001WL | BY110GK OR MS14TB | BY110JK OR MS17TB | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 100 Amp Meter Socket & Circuit Breaker Combination, Underground | Surface | BY111GU | BY116JU OR MM0303F31-00CEY | NA | BY116GU w/UX001WL OR MM0202F11-00CEY w/UX001WL | NA | BY111JU | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 200 Amp Socket Only, Overhead | Surface | BY120GK OR MS24TB | BY120JK OR MS27TB | NA | BY120GK w/UX005B OR MS24TB w/UX005B | BY120GK OR MS24TB | BY120JK OR MS27TB | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 200 Amp Meter Socket & Circuit Breaker Combination, Overhead | Surface | BY125GU OR MM0202L12-00CEY | BY125JU OR MM0303L32-00CEY | NA | BY125GU w/UX005B OR MM0202L12-00CEY w/UX005B | NA | BY125JU OR MM0303L32-00CEY | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 200 Amp Socket Only, Underground | Surface | BY120GK OR MS24TB | BY120JK OR MS27TB | NA | BY120GK w/UX005B OR MS24TB w/UX005B | BY120GK OR MS24TB | BY120JK OR MS27TB | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 200 Amp Meter Socket & Circuit Breaker Combination, Underground | Surface | BY125GU OR MM0202L12-00CEY | BY125JU OR MM0303L3200CEY | NA | BY125GU w/UX005B OR MM0202L12-00CEY w/UX005B | NA | BY125JU OR MM0303L32-00CEY | BY128JU |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 400 Amp Meter Socket & Circuit Breaker Combination, Underground | Surface | NA | NA | NA | NA | NA | NA | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 400 Amp Socket Only, Underground | Surface | NA | NA | NA | NA | NA | NA | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 400 Amp Meter Socket & Circuit Breaker Combination | Surface | NA | NA | NA | NA | NA | NA | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |
| 400 Amp Socket Only, Overhead | Surface | NA | NA | NA | NA | NA | NA | NA |
|  | Flush | NA | NA | NA | NA | NA | NA | NA |

## METER MODULES

## RESIDENTIAL SOCKETS

| Type | Number of Sockets | 125 Amp Breaker Positions, Surface Mtg., Outdoor | 125 Amp Breaker Positions, Semi-Flush mtg., Outdoor | 200 Amp Breaker Positions, Surface Mtg., Outdoor |
| --- | --- | --- | --- | --- |
| All in One | 2-Position | MP2211 | FIELD CONVERTABLE | MP4212 |
|  | 3-Position | MP3311 | FIELD CONVERTABLE | MP4312 |
|  | 4-Position | MP4411 | FIELD CONVERTABLE | MP4412;MP6412 |
|  | 5-Position | MP4511; MP6511 | FIELD CONVERTABLE | MP6512 |
|  | 6-Position | MP4611; MP6611 | FIELD CONVERTABLE | MP6612 |
| Modular | Number of Sockets | 125 Amp Breaker Positions, Indoor | 125 Amp Breaker Positions, Outdoor | 200 Amp Breaker Positions, Outdoor |
|  | 2-Position 1 Phase Cross Buss |  |  | DG232W |
|  | 2-Position 3 Phase Cross Buss |  |  | DG242W |
|  | 3-Position 1 Phase Cross Buss | DG331W | DG331W | DG332W |
|  | 3-Position 3 Phase Cross Buss | DG341W | DG341W | DG342W |
|  | 4-Position 1 Phase Cross Buss | DG431W | DG431W | DG432W |
|  | 4-Position 3 Phase Cross Buss | DG441W | DG441W | DG442W |

# These units only meet utility and EUSERC specifications when NEMA stud kit is added.

## SWITCHBOARD COMMERCIAL MULTIPLE SOCKETS

| Meter Section |
| --- |
| Service Voltage | Amperes | Type |
| 1 PH 3W 3 PH 3W 120/240V 240V or 480V | 400 600 800 1200 1600 2000 | By Gangable CM Switchboard UZ Switchboard |
| 3 PH 4W 208Y/120V 480Y/277V | 400 600 800 1200 1600 2000 | By Gangable CM Switchboard UZ Switchboard |

# TERMINATING PULL SECTIONS

| Service Amperage | All Single Phase Services | All Three Phase Services |
| --- | --- | --- |
| 0 – 200 Amp | APB402W Pull Box UK402A Lug Landing Kit | APB043W Pull Box UK403A Lug Landing Kit |
| 201 – 400 Amp | APB403W Pull Box UK402B Lug Landing Kit | APB803W Pull Box UK403B Lug Landing Kit |
| 401 – 800 Amp | APB802W Pull Box UK802B or UK802C Lug Landing Kit | APB803W Pull Box UK803B or UK803C Lug Landing Kit |
| 801 – 1200 Amp | APB123W Pull Box UK122D Lug Landing Kit | APB123W Pull Box UK123D Lug Landing Kit |

# These units only meet utility and EUSERC specifications when mounting centers are supplied with NEMA terminations.